## Table 1 - Physical Data
Table 1: Physical Data — Johnson Controls Premier 25-50 Ton Rooftop Units (Form 5586959-JIM-A-720)
Category | Item | 25 Ton | 30 Ton | 40 Ton | 50 Ton
Compressor Data - Standard Capacity, Standard Efficiency | Quantity/Size (nominal HP) | 1/4.5, 1/7, 1/10 | 1/5.5, 1/7, 1/7, 1/7.5 | 1/5.5, 1/8.5, 1/10, 1/11.5 | 1/7.5, 1/10, 1/11.5, 1/15
| Type | Scroll | Scroll | Scroll | Scroll
| Capacity Steps | 7 | 11 | 15 | 15
| Number of Circuits | 2 | 2 | 2 | 2
Compressor Data - High Capacity, Standard Efficiency | Quantity/Size (nominal HP) | 1/5, 1/7.5, 1/10 | 1/5.5, 1/7, 1/7, 1/8.5 | 1/7, 1/13, 1/8.5, 1/10 | 1/8.5, 1/15, 1/7.5, 1/15
| Type | Scroll | Scroll | Scroll | Scroll
| Capacity Steps | 7 | 11 | 15 | 11
| Number of Circuits | 2 | 2 | 2 | 2
Compressor Data - Standard Capacity, High Efficiency | Quantity/Size (nominal HP) | 1/5, 1/7.5, 1/13 | 1/7, 1/7, 1/18.5 | 1/7.5, 1/7.5, 1/10, 1/13 | 1/10, 1/10, 1/12, 1/17.5
| Type | Variable Speed Drive or Fixed Scroll | Variable Speed Drive or Fixed Scroll | Variable Speed Drive or Fixed Scroll | Variable Speed Drive or Fixed Scroll
| Capacity Steps | 15-100% | 15-100% | 15-100% | 15-100%
| Number of Circuits | 2 | 2 | 2 | 2
Supply Fan | Quantity of Fans/Motors | 1/1 | 1/1 | 1/1 | 1/1
| Type | Direct Drive Plenum | Direct Drive Plenum | Direct Drive Plenum | Direct Drive Plenum
| Size (inches) | 27 | 27 | 33 | 33
| Motor Size Range (min to max HP) | 5-25 | 5-25 | 10-50 | 10-50
| Airflow Range (min to max CFM) | 5,000-12,000 | 5,000-12,000 | 8,000-20,000 | 8,000-20,000
| Total Static Pressure Range (min to max iwg) | 1.0-8.0 | 1.0-8.0 | 1.0-8.0 | 1.0-8.0
Return Fan | Quantity of Fans/Motors | 1/1 | 1/1 | 1/1 | 1/1
| Type | Belt-Driven Plenum | Belt-Driven Plenum | Belt-Driven Plenum | Belt-Driven Plenum
| Size (inches) | 27 | 27 | 30 | 30
| Motor Size Range (min to max HP) | 5-10 | 5-10 | 5-20 | 5-20
| Airflow Range (min to max CFM) | 5,000-12,000 | 5,000-12,000 | 8,000-20,000 | 8,000-20,000
| Total Static Pressure Range (min to max iwg) | 0.5-3.0 | 0.5-3.0 | 0.5-3.0 | 0.5-3.0
Exhaust Fan | Quantity of Fans/Motors | 1/1 | 1/1 | 1/1 | 1/1
| Type | Belt-Driven Forward Curved | Belt-Driven Forward Curved | Belt-Driven Forward Curved | Belt-Driven Forward Curved
| Size (inches) | 18-18 | 18-18 | 25-25 | 25-25
| Motor Size Range (min to max HP) | 3-15 | 3-15 | 5-20 | 5-20
| Airflow Range (min to max CFM) | 5,000-12,000 | 5,000-12,000 | 8,000-20,000 | 8,000-20,000
| Total Static Pressure Range (min to max iwg) | 0.5-3.0 | 0.5-3.0 | 0.5-3.0 | 0.5-3.0
Condenser Fan | Quantity | 2 | 2 | 4 | 4
| Type | Propeller | Propeller | Propeller | Propeller
| Size (diameter in inches) | 30 | 30 | 30 | 30
| Power (HP) | 2 | 2 | 2 | 2
Evaporator Coil - Standard Capacity, Standard Efficiency | Size (sq. ft.) | 24 | 24 | 36 | 36
| Number of Rows/Fins Per Inch | 3/17 | 5/17 | 4/17 | 4/17
| Size (tube diameter in inches) | 3/8 | 3/8 | 3/8 | 3/8
Evaporator Coil - High Capacity, Standard Efficiency | Size (sq. ft.) | 24 | 24 | 36 | 36
| Number of Rows/Fins Per Inch | 4/17 | 6/17 | 4/17 | 6/17
| Size (tube diameter in inches) | 3/8 | 3/8 | 3/8 | 3/8
Evaporator Coil - Standard Capacity, High Efficiency | Size (sq. ft.) | 24 | 24 | 36 | 36
| Number of Rows/Fins Per Inch | 4/17 | 6/17 | 4/17 | 6/17
| Size (tube diameter in inches) | 3/8 | 3/8 | 3/8 | 3/8
Hot Gas Reheat (HGRH) Coil | Coil Type | Microchannel | Microchannel | Microchannel | Microchannel
| Control Type | Modulating | Modulating | Modulating | Modulating
| Size (area in sq. ft./thickness in inches) | 19.5/0.8 | 19.5/0.8 | 19.5/1 | 19.5/1
| Number of Rows/Fins Per Inch | 1/23 | 1/23 | 1/23 | 1/23
| Minimum OA Temperature for Mechanical Cooling | 45.0°F | 45.0°F | 45.0°F | 45.0°F
| Low Ambient Option Minimum OA Temperature for Mechanical Cooling | -10.0°F | -10.0°F | -10.0°F | -10.0°F
Condenser Coil - Standard Capacity, Standard Efficiency | Size (sq. ft.) | 61 | 61 | 98 | 98
| Number of Rows/Fins Per Inch | 1/23 | 1/23 | 1/23 | 1/23
| Size (thickness in inches) | 0.8 | 0.8 | 0.8 | 1
| Type | Microchannel | Microchannel | Microchannel | Microchannel
Condenser Coil - High Capacity, Standard Efficiency | Size (sq. ft.) | 61 | 61 | 98 | 98
| Number of Rows/Fins Per Inch | 1/23 | 1/23 | 1/23 | 1/23
| Size (thickness in inches) | 0.8 | 0.8 | 0.8 | 1
| Type | Microchannel | Microchannel | Microchannel | Microchannel
Condenser Coil - Standard Capacity, High Efficiency | Size (sq. ft.) | 61 | 61 | 98 | 98
| Number of Rows/Fins Per Inch | 1/23 | 1/23 | 1/23 | 1/23
| Size (thickness in inches) | 1 | 1 | 0.8 | 1
| Type | Microchannel | Microchannel | Microchannel | Microchannel
Energy Recovery Wheel (ERW) - High CFM | Cassette Dimensions (L x W x H in inches) | 50 x 4.36 x 50 | 50 x 4.36 x 50 | 62.42 x 6.07 x 62.42 | 62.42 x 6.07 x 62.42
| Wheel Segments | 6 | 6 | 8 | 8
| Motor (V, ph, Hz) | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60
| Horsepower (HP) | 1/6 | 1/6 | 1/4 | 1/4
| Filter Type | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated
| RA Filters - Size (Number) | 25 x 25 (2) | 25 x 25 (2) | 15 x 20 (6) | 15 x 20 (6)
| OA Filters - Size (Number) | 25 x 25 (2) | 25 x 25 (2) | 15 x 20 (6) | 15 x 20 (6)
Energy Recovery Wheel (ERW) - Low CFM | Cassette Dimensions (L x W x H in inches) | 44 x 4.36 x 44 | 44 x 4.36 x 44 | 56.19 x 4.36 x 56.19 | 56.19 x 4.36 x 56.19
| Wheel Segments | 6 | 6 | 6 | 6
| Motor (V/ph/Hz) | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60 | 208-230/3/60, 460/3/60, 575/3/60
| Horsepower (HP) | 1/6 | 1/6 | 1/6 | 1/6
| Filter Type | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated | 2-inch MERV 8 Pleated
| RA Filters - Size (Number) | 25 x 25 (2) | 25 x 25 (2) | 15 x 20 (6) | 15 x 20 (6)
| OA Filters - Size (Number) | 25 x 25 (2) | 25 x 25 (2) | 15 x 20 (6) | 15 x 20 (6)
Electric Heat (208V/230V) | Size Range - Low/High (kW) | 50/100 | 50/100 | 60/120 | 60/120
| Heating Steps - Low/High | 3/6 | 3/6 | 4/8 | 4/8
Electric Heat (460V/575V) | Size Range - Low/High (kW) | 60/120 | 60/120 | 80/160 | 80/160
| Heating Steps - Low/High | 3/6 | 3/6 | 4/8 | 4/8
Gas Furnace | Staged Furnace Sizes (input/output/stages) | 250 / 202.5 / 2; 500 / 405 / 2; 750 / 607.5 / 4 | 250 / 202.5 / 2; 500 / 405 / 2; 750 / 607.5 / 4 | 500 / 405 / 2; 750 / 607.5 / 4; 1,250 / 1012.5 / 6 | 500 / 405 / 2; 750 / 607.5 / 4; 1,250 / 1012.5 / 6
| Airflow Range (min to max CFM) | 5,000-12,000 | 5,000-12,000 | 8,000-20,000 | 8,000-20,000
| Gas Heat Steady State Efficiency (SSE) | 81% | 81% | 81% | 81%
| Modulating Furnace Sizes (input/output/turndown) | 250 / 202.5 / 10:1; 500 / 405 / 20:1; 750 / 607.5 / 30:1 | 250 / 202.5 / 10:1; 500 / 405 / 20:1; 750 / 607.5 / 30:1 | 500 / 405 / 20:1; 750 / 607.5 / 30:1; 1,250 / 1012.5 / 50:1 | 500 / 405 / 20:1; 750 / 607.5 / 30:1; 1,250 / 1012.5 / 50:1
| Airflow Range (min to max CFM) (Modulating) | 5,000-12,000 | 5,000-12,000 | 8,000-20,000 | 8,000-20,000
Hot Water Coil | Coil Tube Diameter (inches) | 1/2 | 1/2 | 1/2 | 1/2
| Material | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin
| Fins Per Inch - Low/High | 13/10 | 13/10 | 13/10 | 13/10
| Size (H x L in inches) / Rows Low | 25 x 70 / 1 | 25 x 70 / 1 | 42.5 x 70 / 1 | 42.5 x 70 / 1
| Size (H x L in inches) / Rows High | 25 x 70 / 2 | 25 x 70 / 2 | 42.5 x 70 / 2 | 42.5 x 70 / 2
Steam Coil | Coil Tube Diameter (inches) | 1 | 1 | 1 | 1
| Material | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin | Copper Tube/Aluminum Fin
| Fins Per Inch - Low/High | 8/14 | 8/14 | 8/14 | 8/14
| Size (H x L in inches) / Rows Low | 24 x 68 / 1 | 24 x 68 / 1 | 42 x 68 / 1 | 42 x 68 / 1
| Size (H x L in inches) / Rows High | 24 x 68 / 1 | 24 x 68 / 1 | 42 x 68 / 1 | 42 x 68 / 1
Draw-Thru - 2-inch Throwaway Angled Filters | Quantity | 18 | 18 | 24 | 24
| Size (L x W in inches) | 16 x 20 | 16 x 20 | 16 x 20 | 16 x 20
| Total Filter Face Area (sq. ft.) | 40.00 | 40.00 | 53.33 | 53.33
Draw-Thru - 2-inch MERV 8 Angled Filters | Quantity | 18 | 18 | 24 | 24
| Size (L x W in inches) | 16 x 20 | 16 x 20 | 16 x 20 | 16 x 20
| Total Filter Face Area (sq. ft.) | 40.00 | 40.00 | 53.33 | 53.33
Draw-Thru - MERV 15 Bag Filters with 2-inch MERV 8 Pre-Filters | Pre-Filters Quantity | 4 / 6 | 4 / 6 | 8 / 4 | 8 / 4
| Pre-Filters Size (L x W in inches) | 24 x 24 / 16 x 20 | 24 x 24 / 16 x 20 | 24 x 24 / 12 x 24 | 24 x 24 / 12 x 24
| Pre-Filters Total Filter Face Area (sq. ft.) | 29.33 | 29.33 | 40.00 | 40.00
| Bag Filters Quantity | 3 / 3 / 2 / 2 | 3 / 3 / 2 / 2 | 6 / 7 / 2 | 6 / 7 / 2
| Bag Filters Size (L x W in inches) | 24x24 / 24x20 / 12x20 / 12x24 | 24x24 / 24x20 / 12x20 / 12x24 | 24x24 / 12x24 / 12x12 | 24x24 / 12x24 / 12x12
| Bag Filters Total Filter Face Area (sq. ft.) | 29.33 | 29.33 | 40.00 | 40.00
Draw-Thru - MERV 14 Rigid Filters with 2-inch MERV 8 Pre-Filters | Pre-Filters Quantity | 4 / 4 | 4 / 4 | 8 / 4 | 8 / 4
| Pre-Filters Size (L x W in inches) | 24 x 24 / 24 x 20 | 24 x 24 / 24 x 20 | 24 x 24 / 12 x 24 | 24 x 24 / 12 x 24
| Pre-Filters Total Filter Face Area (sq. ft.) | 29.33 | 29.33 | 40.00 | 40.00
| Rigid Filters Quantity | 3 / 3 / 2 / 2 | 3 / 3 / 2 / 2 | 6 / 7 / 2 | 6 / 7 / 2
| Rigid Filters Size (L x W in inches) | 24x24 / 24x20 / 12x20 / 12x24 | 24x24 / 24x20 / 12x20 / 12x24 | 24x24 / 12x24 / 12x12 | 24x24 / 12x24 / 12x12
| Rigid Filters Total Filter Face Area (sq. ft.) | 29.33 | 29.33 | 40.00 | 40.00
Draw-Thru - Vertical 4-inch MERV 8 Filters | Quantity | 6 / 6 | 6 / 6 | 18 | 18
| Size (L x W in inches) | 16 x 25 / 16 x 20 | 16 x 25 / 16 x 20 | 16 x 20 | 16 x 20
| Total Filter Face Area (sq. ft.) | 30.00 | 30.00 | 40.00 | 40.00
Final Filters - MERV 15 Bag Filters with 2-inch Pre-Filters | Pre-Filters Quantity | 4 / 4 | 4 / 4 | 8 / 3 | 8 / 3
| Pre-Filters Size (L x W in inches) | 24 x 24 / 20 x 20 | 24 x 24 / 20 x 20 | 24 x 24 / 12 x 24 | 24 x 24 / 12 x 24
| Pre-Filters Total Filter Face Area (sq. ft.) | 27.11 | 27.11 | 38.00 | 38.00
| Bag Filters Quantity | 3 / 4 / 2 | 3 / 4 / 2 | 6 / 7 | 6 / 7
| Bag Filters Size (L x W in inches) | 24x24 / 20x20 / 12x24 | 24x24 / 20x20 / 12x24 | 24x24 / 12x24 | 24x24 / 12x24
| Bag Filters Total Filter Face Area (sq. ft.) | 27.11 | 27.11 | 38.00 | 38.00
Final Filters - MERV 14 Rigid Filters with 2-inch Pre-Filters | Pre-Filters Quantity | 4 / 4 | 4 / 4 | 8 / 3 | 8 / 3
| Pre-Filters Size (L x W in inches) | 24 x 24 / 20 x 20 | 24 x 24 / 20 x 20 | 24 x 24 / 12 x 24 | 24 x 24 / 12 x 24
| Pre-Filters Total Filter Face Area (sq. ft.) | 27.11 | 27.11 | 38.00 | 38.00
| Rigid Filters Quantity | 3 / 4 / 2 | 3 / 4 / 2 | 6 / 7 | 6 / 7
| Rigid Filters Size (L x W in inches) | 24x24 / 20x20 / 12x24 | 24x24 / 20x20 / 12x24 | 24x24 / 12x24 | 24x24 / 12x24
| Rigid Filters Total Filter Face Area (sq. ft.) | 27.11 | 27.11 | 38.00 | 38.00
Final Filters - MERV 17 HEPA Filters with 2-inch Pre-Filters | Pre-Filters Quantity | 4 / 4 | 4 / 4 | 8 / 3 | 8 / 3
| Pre-Filters Size (L x W in inches) | 24 x 24 / 20 x 20 | 24 x 24 / 20 x 20 | 24 x 24 / 12 x 24 | 24 x 24 / 12 x 24
| Pre-Filters Total Filter Face Area (sq. ft.) | 27.11 | 27.11 | 38.00 | 38.00
| HEPA Filters Quantity | 6.00 | 6.00 | 15 / 3 | 15 / 3
| HEPA Filters Size (L x W in inches) | 24 x 24 | 24 x 24 | 12 x 24 / 12 x 17 | 12 x 24 / 12 x 17
| HEPA Filters Total Filter Face Area (sq. ft.) | 24.00 | 24.00 | 34.26 | 34.26