## Slide 1
IMAP Charge Prediction
IMAP — Integrated Modeling & Analysis Platform
≈9%
of lab test time spent on charge optimization
Product family | Dual Fuel Heat Pump |  |  |  | Standard Efficiency Unit |  |  |  |  | High Efficiency Unit |  |  | 
Tonnage | 12.5 | 15 | 20 | 25 | 15 | 17.5 | 20 | 25 | 27.5 | 15 | 17.5 | 20 | 23
Charge optimization (days) | 17 | 9 | 14 | 17 | 10 | 10 | 4 | 15 | 15 | 8 | 11 | 7 | 10
Test duration (days) | 140 | 138 | 150 | 143 | 150 | 111 | 54 | 141 | 160 | 109 | 133 | 94 | 133
Charge optimization % of total | 12.1% | 6.5% | 9.3% | 11.9% | 6.7% | 9.0% | 7.4% | 10.6% | 9.4% | 7.3% | 8.2% | 7.4% | 7.5%
Average | 10.0% |  |  |  | 8.6% |  |  |  |  | 7.6% |  |  | 
Impact on Dual Fuel Heat Pump test plan
Parameter | Before — accuracy 80–85% |  |  |  | After — accuracy 95–97% |  |  | 
Tonnage | 12.5 | 15 | 20 | 25 | 12.5 | 15 | 20 | 25
Charge opt. days | 17 | 9 | 14 | 17 | 4 | 0 | 0 | 5
Test duration (days) | 140 | 138 | 150 | 143 | 127 | 0 | 0 | 129
Total days, all units | 571 |  |  |  | 256 |  |  | 
In-between 15 & 20 ton units removed from lab testing — charge predicted by IMAP at 95–97% accuracy.
≈50%
reduction in total test days
571 → 256 days
Avg. % difference vs. lab
Heat Pump unit: 17%
Cooling unit: 20%
ROOT CAUSE — IMAP GAP
IMAP charge prediction accuracy today: ~80–85%
Gap to close: 10–13 pts (target 95–97%)
✓ More lab slots — higher utilization of test chambers
✓ Faster product development cycles
✓ Benefit scales to every future unit tested